{"text_format":"1","workbook":"xlsx","n_sheets":6,"sheets":["Device_Configuration","Overall","435_490_Configuration","Serial_Configuration","TCPIP_Configuration","Product_Selector"],"not_rendered":{"charts":0,"images":1,"macros":1,"external_links":0,"defined_names":43,"comments":0,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Device_Configuration","index":0,"n_rows":426,"n_cols":6,"rows_kept":426,"cut":false,"hidden":false,"merged":[[389,3,389,18],[406,3,406,18],[407,3,407,18],[408,3,408,18],[409,3,409,18],[410,3,410,18],[401,3,401,18],[111,3,111,18],[112,3,112,18],[124,3,124,18],[125,3,125,18],[119,3,119,18],[120,3,120,18],[121,3,121,18],[122,3,122,18],[123,3,123,18],[113,3,113,18],[114,3,114,18],[115,3,115,18],[116,3,116,18],[117,3,117,18],[385,3,385,18],[386,3,386,18],[387,3,387,18],[422,3,422,18],[423,3,423,18],[424,3,424,18],[425,3,425,18],[397,3,397,18],[398,3,398,18],[399,3,399,18],[400,3,400,18],[390,3,390,18],[391,3,391,18],[392,3,392,18],[393,3,393,18],[394,3,394,18],[395,3,395,18],[402,3,402,18],[403,3,403,18],[404,3,404,18],[405,3,405,18],[417,3,417,18],[418,3,418,18],[419,3,419,18],[420,3,420,18],[421,3,421,18],[411,3,411,18],[63,3,63,18],[64,3,64,18],[65,3,65,18],[66,3,66,18],[84,3,84,18],[85,3,85,18],[87,3,87,18],[88,3,88,18],[89,3,89,18],[82,3,82,18],[370,3,370,18],[358,3,358,18],[359,3,359,18],[360,3,360,18],[361,3,361,18],[362,3,362,18],[352,3,352,18],[354,3,354,18],[355,3,355,18],[412,3,412,18],[414,3,414,18],[415,3,415,18],[416,3,416,18],[371,3,371,18],[372,3,372,18],[373,3,373,18],[363,3,363,18],[364,3,364,18],[365,3,365,18],[367,3,367,18],[368,3,368,18],[388,3,388,18],[379,3,379,18],[380,3,380,18],[381,3,381,18],[382,3,382,18],[384,3,384,18],[374,3,374,18],[375,3,375,18],[376,3,376,18],[377,3,377,18],[378,3,378,18],[369,3,369,18],[356,3,356,18],[357,3,357,18],[347,3,347,18],[348,3,348,18],[349,3,349,18],[350,3,350,18],[351,3,351,18],[342,3,342,18],[343,3,343,18],[344,3,344,18],[345,3,345,18],[346,3,346,18],[337,3,337,18],[338,3,338,18],[339,3,339,18],[340,3,340,18],[341,3,341,18],[331,3,331,18],[332,3,332,18],[333,3,333,18],[334,3,334,18],[335,3,335,18],[326,3,326,18],[327,3,327,18],[328,3,328,18],[329,3,329,18],[330,3,330,18],[320,3,320,18],[321,3,321,18],[322,3,322,18],[324,3,324,18],[325,3,325,18],[315,3,315,18],[316,3,316,18],[317,3,317,18],[318,3,318,18],[319,3,319,18],[310,3,310,18],[311,3,311,18],[312,3,312,18],[313,3,313,18],[314,3,314,18],[304,3,304,18],[305,3,305,18],[307,3,307,18],[308,3,308,18],[309,3,309,18],[299,3,299,18],[300,3,300,18],[301,3,301,18],[302,3,302,18],[303,3,303,18],[294,3,294,18],[295,3,295,18],[296,3,296,18],[297,3,297,18],[298,3,298,18],[288,3,288,18],[289,3,289,18],[290,3,290,18],[291,3,291,18],[292,3,292,18],[283,3,283,18],[284,3,284,18],[285,3,285,18],[286,3,286,18],[287,3,287,18],[278,3,278,18],[279,3,279,18],[280,3,280,18],[281,3,281,18],[282,3,282,18],[272,3,272,18],[273,3,273,18],[274,3,274,18],[275,3,275,18],[277,3,277,18],[267,3,267,18],[268,3,268,18],[269,3,269,18],[270,3,270,18],[271,3,271,18],[261,3,261,18],[262,3,262,18],[264,3,264,18],[265,3,265,18],[266,3,266,18],[256,3,256,18],[257,3,257,18],[258,3,258,18],[259,3,259,18],[260,3,260,18],[251,3,251,18],[252,3,252,18],[253,3,253,18],[254,3,254,18],[255,3,255,18],[245,3,245,18],[247,3,247,18],[248,3,248,18],[249,3,249,18],[250,3,250,18],[240,3,240,18],[241,3,241,18],[242,3,242,18],[243,3,243,18],[244,3,244,18],[235,3,235,18],[236,3,236,18],[237,3,237,18],[238,3,238,18],[239,3,239,18],[229,3,229,18],[230,3,230,18],[231,3,231,18],[232,3,232,18],[234,3,234,18],[224,3,224,18],[225,3,225,18],[226,3,226,18],[227,3,227,18],[228,3,228,18],[219,3,219,18],[220,3,220,18],[221,3,221,18],[222,3,222,18],[223,3,223,18],[213,3,213,18],[214,3,214,18],[215,3,215,18],[217,3,217,18],[218,3,218,18],[208,3,208,18],[209,3,209,18],[210,3,210,18],[211,3,211,18],[212,3,212,18],[202,3,202,18],[204,3,204,18],[205,3,205,18],[206,3,206,18],[207,3,207,18],[197,3,197,18],[198,3,198,18],[199,3,199,18],[200,3,200,18],[201,3,201,18],[192,3,192,18],[193,3,193,18],[194,3,194,18],[195,3,195,18],[196,3,196,18],[187,3,187,18],[188,3,188,18],[189,3,189,18],[190,3,190,18],[191,3,191,18],[184,3,184,18],[185,3,185,18],[129,3,129,18],[130,3,130,18],[131,3,131,18],[132,3,132,18],[133,3,133,18],[136,3,136,18],[139,3,139,18],[140,3,140,18],[141,3,141,18],[142,3,142,18],[157,3,157,18],[174,3,174,18],[179,3,179,18],[180,3,180,18],[181,3,181,18],[182,3,182,18],[183,3,183,18],[172,3,172,18],[175,3,175,18],[176,3,176,18],[177,3,177,18],[178,3,178,18],[167,3,167,18],[168,3,168,18],[169,3,169,18],[170,3,170,18],[171,3,171,18],[162,3,162,18],[163,3,163,18],[164,3,164,18],[165,3,165,18],[166,3,166,18],[155,3,155,18],[158,3,158,18],[159,3,159,18],[160,3,160,18],[161,3,161,18],[38,3,38,18],[151,3,151,18],[152,3,152,18],[153,3,153,18],[154,3,154,18],[145,3,145,18],[146,3,146,18],[147,3,147,18],[148,3,148,18],[149,3,149,18],[150,3,150,18],[79,3,79,18],[80,3,80,18],[81,3,81,18],[50,3,50,18],[53,3,53,18],[52,3,52,18],[51,3,51,18],[48,3,48,18],[56,3,56,18],[107,3,107,18],[108,3,108,18],[109,3,109,18],[101,3,101,18],[83,3,83,18],[73,3,73,18],[74,3,74,18],[75,3,75,18],[76,3,76,18],[77,3,77,18],[90,3,90,18],[91,3,91,18],[92,3,92,18],[93,3,93,18],[95,3,95,18],[127,3,127,18],[144,3,144,18],[134,3,134,18],[128,3,128,18],[135,3,135,18],[137,3,137,18],[138,3,138,18],[104,3,104,18],[105,3,105,18],[106,3,106,18],[96,3,96,18],[97,3,97,18],[98,3,98,18],[99,3,99,18],[100,3,100,18],[103,3,103,18],[0,0,2,2],[8,3,8,18],[9,3,9,18],[10,3,10,18],[12,3,12,18],[11,3,11,18],[7,3,7,18],[40,3,40,18],[39,3,39,18],[21,3,21,18],[29,3,29,18],[14,3,14,18],[15,3,15,18],[16,3,16,18],[17,3,17,18],[18,3,18,18],[22,3,22,18],[23,3,23,18],[24,3,24,18],[25,3,25,18],[26,3,26,18],[27,3,27,18],[30,3,30,18],[36,3,36,18],[19,3,19,18],[67,3,67,18],[68,3,68,18],[69,3,69,18],[71,3,71,18],[72,3,72,18],[47,3,47,18],[55,3,55,18],[49,3,49,18],[44,3,44,18],[45,3,45,18],[61,3,61,18],[57,3,57,18],[58,3,58,18],[59,3,59,18],[60,3,60,18],[41,3,41,18],[42,3,42,18],[43,3,43,18],[31,3,31,18],[32,3,32,18],[33,3,33,18],[34,3,34,18],[35,3,35,18]]}
[null,null,null,"Device Configuration "]
[null,null,null,"Real Time Automation, Inc.    All Rights Reserved"]
[null,null,null,"Support@rtaautomation.com",null,"1-800-249-1612"]
["Product","Value",null,"Note: Enable Macros in Excel"]
["Selector","435NBX-N700","N700"]
["Application Name","Location / Application"]
[]
["Ethernet Port 0","Value",null,"Help Descriptions"]
["IP Address","0.0.0.0",null,"IP Address of the Gateway: This will not change the IP Address of the Gateway"]
["Subnet","0.0.0.0",null,"Subnet of the Gateway: This will not change the Subnet of the Gateway"]
["Default Gateway","0.0.0.0",null,"Default Gateway of the Gateway: This will not change the Default Gateway of the Gateway"]
["DNS Gateway","0.0.0.0",null,"DNS Gateway of the Gateway: This will not change the DNS of the Gateway"]
["Ethernet Link","Auto Negotiate"]
[]
["Ethernet Port 1","Value",null,"Help Descriptions"]
["IP Address","0.0.0.0",null,"IP Address of the Gateway: This will not change the IP Address of the Gateway"]
["Subnet","0.0.0.0",null,"Subnet of the Gateway: This will not change the Subnet of the Gateway"]
["Default Gateway","0.0.0.0",null,"Default Gateway of the Gateway: This will not change the Default Gateway of the Gateway"]
["DNS Gateway","0.0.0.0",null,"DNS Gateway of the Gateway: This will not change the DNS of the Gateway"]
["Auto-Negotiate","Auto Negotiate"]
[]
["435 / 490 PLC ","Value",null,"Help Descriptions"]
["PLC Type","None",null,"Select the PLC Type that is being used"]
["IP Address","0.0.0.0",null,"Enter the IP Address of the PLC"]
["Controller Slot",0,null,"Enter the Slot that the Controller is in. If using an Integrated Ethernet Card, Slot is 0"]
["Communication Mode","Class 3",null,"Select UCMM for Unconnected messaging (relies on shared resources) and Class 3 for Connected messaging (relies on reserved resources)"]
["Inter-Message Delay",0,null,"Enter a value, in milliseconds, that will slow down the communication between the gateway and the PLC"]
["Heartbeat Tag/File",null,null,"Enter an INT Tag / File to be used to determine that the gateway is running"]
[]
["Serial Port 0 ","Value",null,"Help Descriptions"]
["Enabled","Enabled"]
["Communication Mode","RS232",null,"Must match the ASCII device"]
["Baud Rate",19200,null,"Must match the ASCII device"]
["Data Bits",8,null,"Must match the ASCII device"]
["Stop Bits",1,null,"Must match the ASCII device"]
["Parity","NONE",null,"Must match the ASCII device"]
["Flow Control","NONE"]
[]
["Serial Port 1","Value",null,"Help Descriptions"]
["Enabled","Enabled"]
["Communication Mode","RS232",null,"Must match the ASCII device"]
["Baud Rate",19200,null,"Must match the ASCII device"]
["Data Bits",8,null,"Must match the ASCII device"]
["Stop Bits",1,null,"Must match the ASCII device"]
["Parity","NONE",null,"Must match the ASCII device"]
["Flow Control","NONE"]
[]
["TCP/IP Port 0","Value",null,"Help Descriptions"]
["Enable","Enabled"]
["Client","Enabled",null,"Enabled is the gateway acting as a TCP/IP Client (your device is a TCP/IP Server)"]
["IP Address","0.0.0.0",null,"If Client is enabled, this is the IP Address of the Server device. If Client is disabled and IP is 0.0.0.0, the gateway will accept a connection from any IP Address or if IP is not 0.0.0.0, it will only accept that IP"]
["Port",0," ","TCP Port that the TCP/IP connection is made on"]
["Inactivity Timeout",5,null,"Amount of time, in seconds, that the gateway will wait to keep the connection. If the time expires, the connection will be closed"]
["Reconnect Delay",10,null,"If Client is enabled, the amount of time, in seconds, that the gateway will wait to make a new connection"]
[]
["TCP/IP Port 1","Value",null,"Help Descriptions"]
["Enable","Disabled"]
["Client","Enabled",null,"Enabled is the gateway acting as a TCP/IP Client (your device is a TCP/IP Server)"]
["IP Address","0.0.0.0",null,"If Client is enabled, this is the IP Address of the Server device. If Client is disabled and IP is 0.0.0.0, the gateway will accept a connection from any IP Address or if IP is not 0.0.0.0, it will only accept that IP"]
["Port",0,null,"TCP Port that the TCP/IP connection is made on"]
["Inactivity Timeout",5,null,"Amount of time, in seconds, that the gateway will wait to keep the connection. If the time expires, the connection will be closed"]
["Reconnect Delay",10,null,"If Client is enabled, the amount of time, in seconds, that the gateway will wait to make a new connection"]
[]
["TCP/IP Port 2","Value",null,"Help Descriptions"]
["Enable","Disabled"]
["Client","Enabled",null,"Enabled is the gateway acting as a TCP/IP Client (your device is a TCP/IP Server)"]
["IP Address","0.0.0.0",null,"If Client is enabled, this is the IP Address of the Server device. If Client is disabled and IP is 0.0.0.0, the gateway will accept a connection from any IP Address or if IP is not 0.0.0.0, it will only accept that IP"]
["Port",0,null,"TCP Port that the TCP/IP connection is made on"]
["Inactivity Timeout",5,null,"Amount of time, in seconds, that the gateway will wait to keep the connection. If the time expires, the connection will be closed"]
["Reconnect Delay",10,null,"If Client is enabled, the amount of time, in seconds, that the gateway will wait to make a new connection"]
[]
["TCP/IP Port 3","Value",null,"Help Descriptions"]
["Enable","Disabled"]
["Client","Enabled",null,"Enabled is the gateway acting as a TCP/IP Client (your device is a TCP/IP Server)"]
["IP Address","0.0.0.0",null,"If Client is enabled, this is the IP Address of the Server device. If Client is disabled and IP is 0.0.0.0, the gateway will accept a connection from any IP Address or if IP is not 0.0.0.0, it will only accept that IP"]
["Port",0,null,"TCP Port that the TCP/IP connection is made on"]
["Inactivity Timeout",5,null,"Amount of time, in seconds, that the gateway will wait to keep the connection. If the time expires, the connection will be closed"]
["Reconnect Delay",10,null,"If Client is enabled, the amount of time, in seconds, that the gateway will wait to make a new connection"]
[]
["TCP/IP Port 4","Value",null,"Help Descriptions"]
["Enable","Disabled"]
["Client","Enabled",null,"Enabled is the gateway acting as a TCP/IP Client (your device is a TCP/IP Server)"]
["IP Address","0.0.0.0",null,"If Client is enabled, this is the IP Address of the Server device. If Client is disabled and IP is 0.0.0.0, the gateway will accept a connection from any IP Address or if IP is not 0.0.0.0, it will only accept that IP"]
["Port",0,null,"TCP Port that the TCP/IP connection is made on"]
["Inactivity Timeout",5,null,"Amount of time, in seconds, that the gateway will wait to keep the connection. If the time expires, the connection will be closed"]
["Reconnect Delay",10,null,"If Client is enabled, the amount of time, in seconds, that the gateway will wait to make a new connection"]
[]
["TCP/IP Port 5","Value",null,"Help Descriptions"]
["Enable","Disabled"]
["Client","Enabled",null,"Enabled is the gateway acting as a TCP/IP Client (your device is a TCP/IP Server)"]
["IP Address","0.0.0.0",null,"If Client is enabled, this is the IP Address of the Server device. If Client is disabled and IP is 0.0.0.0, the gateway will accept a connection from any IP Address or if IP is not 0.0.0.0, it will only accept that IP"]
["Port",0,null,"TCP Port that the TCP/IP connection is made on"]
["Inactivity Timeout",5,null,"Amount of time, in seconds, that the gateway will wait to keep the connection. If the time expires, the connection will be closed"]
["Reconnect Delay",10,null,"If Client is enabled, the amount of time, in seconds, that the gateway will wait to make a new connection"]
[]
["TCP/IP Port 6","Value",null,"Help Descriptions"]
["Enable","Disabled"]
["Client","Enabled",null,"Enabled is the gateway acting as a TCP/IP Client (your device is a TCP/IP Server)"]
["IP Address","0.0.0.0",null,"If Client is enabled, this is the IP Address of the Server device. If Client is disabled and IP is 0.0.0.0, the gateway will accept a connection from any IP Address or if IP is not 0.0.0.0, it will only accept that IP"]
["Port",0,null,"TCP Port that the TCP/IP connection is made on"]
["Inactivity Timeout",5,null,"Amount of time, in seconds, that the gateway will wait to keep the connection. If the time expires, the connection will be closed"]
["Reconnect Delay",10,null,"If Client is enabled, the amount of time, in seconds, that the gateway will wait to make a new connection"]
[]
["TCP/IP Port 7","Value",null,"Help Descriptions"]
["Enable","Disabled"]
["Client","Enabled",null,"Enabled is the gateway acting as a TCP/IP Client (your device is a TCP/IP Server)"]
["IP Address","0.0.0.0",null,"If Client is enabled, this is the IP Address of the Server device. If Client is disabled and IP is 0.0.0.0, the gateway will accept a connection from any IP Address or if IP is not 0.0.0.0, it will only accept that IP"]
["Port",0,null,"TCP Port that the TCP/IP connection is made on"]
["Inactivity Timeout",5,null,"Amount of time, in seconds, that the gateway will wait to keep the connection. If the time expires, the connection will be closed"]
["Reconnect Delay",10,null,"If Client is enabled, the amount of time, in seconds, that the gateway will wait to make a new connection"]
[]
["TCP/IP Port 8","Value",null,"Help Descriptions"]
["Enable","Disabled"]
["Client","Enabled",null,"Enabled is the gateway acting as a TCP/IP Client (your device is a TCP/IP Server)"]
["IP Address","0.0.0.0",null,"If Client is enabled, this is the IP Address of the Server device. If Client is disabled and IP is 0.0.0.0, the gateway will accept a connection from any IP Address or if IP is not 0.0.0.0, it will only accept that IP"]
["Port",0,null,"TCP Port that the TCP/IP connection is made on"]
["Inactivity Timeout",5,null,"Amount of time, in seconds, that the gateway will wait to keep the connection. If the time expires, the connection will be closed"]
["Reconnect Delay",10,null,"If Client is enabled, the amount of time, in seconds, that the gateway will wait to make a new connection"]
[]
["TCP/IP Port 9","Value",null,"Help Descriptions"]
["Enable","Disabled"]
["Client","Enabled",null,"Enabled is the gateway acting as a TCP/IP Client (your device is a TCP/IP Server)"]
["IP Address","0.0.0.0",null,"If Client is enabled, this is the IP Address of the Server device. If Client is disabled and IP is 0.0.0.0, the gateway will accept a connection from any IP Address or if IP is not 0.0.0.0, it will only accept that IP"]
["Port",0,null,"TCP Port that the TCP/IP connection is made on"]
["Inactivity Timeout",5,null,"Amount of time, in seconds, that the gateway will wait to keep the connection. If the time expires, the connection will be closed"]
["Reconnect Delay",10,null,"If Client is enabled, the amount of time, in seconds, that the gateway will wait to make a new connection"]
[]
["435 / 490 ASCII to PLC Port 0","Value",null,"Help Descriptions"]
["Enabled","Enabled"]
["Data Type","STRING",null,"Data Type of the Tag / File in the PLC"]
["Tag / File Name",null,null,"Controller Scope Tag / File defined in the PLC. If using Program Scope Tag, refer to Appendix D in the userguide"]
["Character Count",82,null,"End Case 1: Max number of characters that can be received to call a message complete. If above 82 and a STRING data type used, refer to Appendix C in the userguide"]
["Timer",0,null,"End Case 2: Max number of time, in milliseconds, that the gateway will wait between receiving ASCII characters. If the time expires, the message is called complete"]
["Start Delimiter Count",0,null,"End Case 3: ASCII message has common start delimiters at the beginning of every message"]
["Start Delimiter 1","[NUL] 0 0x00"]
["Start Delimiter 2","[NUL] 0 0x00"]
["End Delimiter Count",0,null,"End Case 3: ASCII message has common end delimiters at the beginning of every message"]
["End Delimiter 1","[NUL] 0 0x00"]
["End Delimiter 2","[NUL] 0 0x00"]
["Remove Delimiters","Disabled",null,"If using Start or End Delimiters and you don't want them transferred to the PLC, enable this option"]
["Queue Size",5,null,"Enter in the number of complete messages that you want the gateway to hold on to"]
["Queue Full Behavior","Discard New Data",null,"Based on the Queue Size, if the Queue is full, the gateway will discard messaages based on this option"]
["NULL Character Handling","None",null,"Remove all NULL characters prior to sending the message to the PLC"]
[]
["435 / 490 PLC to ASCII Port 0","Value",null,"Help Descriptions"]
["Enabled","Enabled"]
["Data Type","STRING",null,"Data Type of the Tag / File in the PLC"]
["Tag / File Name",null,null,"Controller Scope Tag / File defined in the PLC. If using Program Scope Tag, refer to Appendix D in the userguide"]
["Character Count",82,null,"Max number of characters that can be received from the PLC. If above 82 and a STRING data type used, refer to Appendix C in the userguide"]
["Start Delimiter Count",0,null,"If the ASCII message has common start delimiters at the beginning of every message, then the gateway can be configured for up to 2 start delimiters"]
["Start Delimiter 1","[NUL] 0 0x00"]
["Start Delimiter 2","[NUL] 0 0x00"]
["End Delimiter Count",0,null,"If the ASCII message has common end delimiters at the end of every message, then the gateway can be configured for up to 2 end delimiters"]
["End Delimiter 1","[NUL] 0 0x00"]
["End Delimiter 2","[NUL] 0 0x00"]
["NULL Character Handling","None",null,"Prepend or Postpend a NULL character to each character to be sent to the ASCII message"]
[]
["435 / 490 ASCII to PLC Port 1","Value",null,"Help Descriptions"]
["Enabled","Enabled"]
["Data Type","STRING",null,"Data Type of the Tag / File in the PLC"]
["Tag / File Name",null,null,"Controller Scope Tag / File defined in the PLC. If using Program Scope Tag, refer to Appendix D in the userguide"]
["Character Count",82,null,"End Case 1: Max number of characters that can be received to call a message complete. If above 82 and a STRING data type used, refer to Appendix C in the userguide"]
["Timer",0,null,"End Case 2: Max number of time, in milliseconds, that the gateway will wait between receiving ASCII characters. If the time expires, the message is called complete"]
["Start Delimiter Count",0,null,"End Case 3: ASCII message has common start delimiters at the beginning of every message"]
["Start Delimiter 1","[NUL] 0 0x00"]
["Start Delimiter 2","[NUL] 0 0x00"]
["End Delimiter Count",0,null,"End Case 3: ASCII message has common end delimiters at the beginning of every message"]
["End Delimiter 1","[NUL] 0 0x00"]
["End Delimiter 2","[NUL] 0 0x00"]
["Remove Delimiters","Disabled",null,"If using Start or End Delimiters and you don't want them transferred to the PLC, enable this option"]
["Queue Size",5,null,"Enter in the number of complete messages that you want the gateway to hold on to"]
["Queue Full Behavior","Discard New Data",null,"Based on the Queue Size, if the Queue is full, the gateway will discard messaages based on this option"]
["NULL Character Handling","None",null,"Remove all NULL characters prior to sending the message to the PLC"]
[]
["435 / 490 PLC to ASCII Port 1","Value",null,"Help Descriptions"]
["Enabled","Enabled"]
["Data Type","STRING",null,"Data Type of the Tag / File in the PLC"]
["Tag / File Name",null,null,"Controller Scope Tag / File defined in the PLC. If using Program Scope Tag, refer to Appendix D in the userguide"]
["Character Count",82,null,"Max number of characters that can be received from the PLC. If above 82 and a STRING data type used, refer to Appendix C in the userguide"]
["Start Delimiter Count",0,null,"If the ASCII message has common start delimiters at the beginning of every message, then the gateway can be configured for up to 2 start delimiters"]
["Start Delimiter 1","[NUL] 0 0x00"]
["Start Delimiter 2","[NUL] 0 0x00"]
["End Delimiter Count",0,null,"If the ASCII message has common end delimiters at the end of every message, then the gateway can be configured for up to 2 end delimiters"]
["End Delimiter 1","[NUL] 0 0x00"]
["End Delimiter 2","[NUL] 0 0x00"]
["NULL Character Handling","None",null,"Prepend or Postpend a NULL character to each character to be sent to the ASCII message"]
[]
["435 / 490 ASCII to PLC Port 2","Value",null,"Help Descriptions"]
["Enabled","Enabled"]
["Data Type","STRING",null,"Data Type of the Tag / File in the PLC"]
["Tag / File Name",null,null,"Controller Scope Tag / File defined in the PLC. If using Program Scope Tag, refer to Appendix D in the userguide"]
["Character Count",82,null,"End Case 1: Max number of characters that can be received to call a message complete. If above 82 and a STRING data type used, refer to Appendix C in the userguide"]
["Timer",0,null,"End Case 2: Max number of time, in milliseconds, that the gateway will wait between receiving ASCII characters. If the time expires, the message is called complete"]
["Start Delimiter Count",0,null,"End Case 3: ASCII message has common start delimiters at the beginning of every message"]
["Start Delimiter 1","[NUL] 0 0x00"]
["Start Delimiter 2","[NUL] 0 0x00"]
["End Delimiter Count",0,null,"End Case 3: ASCII message has common end delimiters at the beginning of every message"]
["End Delimiter 1","[NUL] 0 0x00"]
["End Delimiter 2","[NUL] 0 0x00"]
["Remove Delimiters","Disabled",null,"If using Start or End Delimiters and you don't want them transferred to the PLC, enable this option"]
["Queue Size",5,null,"Enter in the number of complete messages that you want the gateway to hold on to"]
["Queue Full Behavior","Discard New Data",null,"Based on the Queue Size, if the Queue is full, the gateway will discard messaages based on this option"]
["NULL Character Handling","None",null,"Remove all NULL characters prior to sending the message to the PLC"]
[]
["435 / 490 PLC to ASCII Port 2","Value",null,"Help Descriptions"]
["Enabled","Enabled"]
["Data Type","STRING",null,"Data Type of the Tag / File in the PLC"]
["Tag / File Name",null,null,"Controller Scope Tag / File defined in the PLC. If using Program Scope Tag, refer to Appendix D in the userguide"]
["Character Count",82,null,"Max number of characters that can be received from the PLC. If above 82 and a STRING data type used, refer to Appendix C in the userguide"]
["Start Delimiter Count",0,null,"If the ASCII message has common start delimiters at the beginning of every message, then the gateway can be configured for up to 2 start delimiters"]
["Start Delimiter 1","[NUL] 0 0x00"]
["Start Delimiter 2","[NUL] 0 0x00"]
["End Delimiter Count",0,null,"If the ASCII message has common end delimiters at the end of every message, then the gateway can be configured for up to 2 end delimiters"]
["End Delimiter 1","[NUL] 0 0x00"]
["End Delimiter 2","[NUL] 0 0x00"]
["NULL Character Handling","None",null,"Prepend or Postpend a NULL character to each character to be sent to the ASCII message"]
[]
["435 / 490 ASCII to PLC Port 3","Value",null,"Help Descriptions"]
["Enabled","Enabled"]
["Data Type","STRING",null,"Data Type of the Tag / File in the PLC"]
["Tag / File Name",null,null,"Controller Scope Tag / File defined in the PLC. If using Program Scope Tag, refer to Appendix D in the userguide"]
["Character Count",82,null,"End Case 1: Max number of characters that can be received to call a message complete. If above 82 and a STRING data type used, refer to Appendix C in the userguide"]
["Timer",0,null,"End Case 2: Max number of time, in milliseconds, that the gateway will wait between receiving ASCII characters. If the time expires, the message is called complete"]
["Start Delimiter Count",0,null,"End Case 3: ASCII message has common start delimiters at the beginning of every message"]
["Start Delimiter 1","[NUL] 0 0x00"]
["Start Delimiter 2","[NUL] 0 0x00"]
["End Delimiter Count",0,null,"End Case 3: ASCII message has common end delimiters at the beginning of every message"]
["End Delimiter 1","[NUL] 0 0x00"]
["End Delimiter 2","[NUL] 0 0x00"]
["Remove Delimiters","Disabled",null,"If using Start or End Delimiters and you don't want them transferred to the PLC, enable this option"]
["Queue Size",5,null,"Enter in the number of complete messages that you want the gateway to hold on to"]
["Queue Full Behavior","Discard New Data",null,"Based on the Queue Size, if the Queue is full, the gateway will discard messaages based on this option"]
["NULL Character Handling","None",null,"Remove all NULL characters prior to sending the message to the PLC"]
[]
["435 / 490 PLC to ASCII Port 3","Value",null,"Help Descriptions"]
["Enabled","Enabled"]
["Data Type","STRING",null,"Data Type of the Tag / File in the PLC"]
["Tag / File Name",null,null,"Controller Scope Tag / File defined in the PLC. If using Program Scope Tag, refer to Appendix D in the userguide"]
["Character Count",82,null,"Max number of characters that can be received from the PLC. If above 82 and a STRING data type used, refer to Appendix C in the userguide"]
["Start Delimiter Count",0,null,"If the ASCII message has common start delimiters at the beginning of every message, then the gateway can be configured for up to 2 start delimiters"]
["Start Delimiter 1","[NUL] 0 0x00"]
["Start Delimiter 2","[NUL] 0 0x00"]
["End Delimiter Count",0,null,"If the ASCII message has common end delimiters at the end of every message, then the gateway can be configured for up to 2 end delimiters"]
["End Delimiter 1","[NUL] 0 0x00"]
["End Delimiter 2","[NUL] 0 0x00"]
["NULL Character Handling","None",null,"Prepend or Postpend a NULL character to each character to be sent to the ASCII message"]
[]
["435 / 490 ASCII to PLC Port 4","Value",null,"Help Descriptions"]
["Enabled","Enabled"]
["Data Type","STRING",null,"Data Type of the Tag / File in the PLC"]
["Tag / File Name",null,null,"Controller Scope Tag / File defined in the PLC. If using Program Scope Tag, refer to Appendix D in the userguide"]
["Character Count",82,null,"End Case 1: Max number of characters that can be received to call a message complete. If above 82 and a STRING data type used, refer to Appendix C in the userguide"]
["Timer",0,null,"End Case 2: Max number of time, in milliseconds, that the gateway will wait between receiving ASCII characters. If the time expires, the message is called complete"]
["Start Delimiter Count",0,null,"End Case 3: ASCII message has common start delimiters at the beginning of every message"]
["Start Delimiter 1","[NUL] 0 0x00"]
["Start Delimiter 2","[NUL] 0 0x00"]
["End Delimiter Count",0,null,"End Case 3: ASCII message has common end delimiters at the beginning of every message"]
["End Delimiter 1","[NUL] 0 0x00"]
["End Delimiter 2","[NUL] 0 0x00"]
["Remove Delimiters","Disabled",null,"If using Start or End Delimiters and you don't want them transferred to the PLC, enable this option"]
["Queue Size",5,null,"Enter in the number of complete messages that you want the gateway to hold on to"]
["Queue Full Behavior","Discard New Data",null,"Based on the Queue Size, if the Queue is full, the gateway will discard messaages based on this option"]
["NULL Character Handling","None",null,"Remove all NULL characters prior to sending the message to the PLC"]
[]
["435 / 490 PLC to ASCII Port 4","Value",null,"Help Descriptions"]
["Enabled","Enabled"]
["Data Type","STRING",null,"Data Type of the Tag / File in the PLC"]
["Tag / File Name",null,null,"Controller Scope Tag / File defined in the PLC. If using Program Scope Tag, refer to Appendix D in the userguide"]
["Character Count",82,null,"Max number of characters that can be received from the PLC. If above 82 and a STRING data type used, refer to Appendix C in the userguide"]
["Start Delimiter Count",0,null,"If the ASCII message has common start delimiters at the beginning of every message, then the gateway can be configured for up to 2 start delimiters"]
["Start Delimiter 1","[NUL] 0 0x00"]
["Start Delimiter 2","[NUL] 0 0x00"]
["End Delimiter Count",0,null,"If the ASCII message has common end delimiters at the end of every message, then the gateway can be configured for up to 2 end delimiters"]
["End Delimiter 1","[NUL] 0 0x00"]
["End Delimiter 2","[NUL] 0 0x00"]
["NULL Character Handling","None",null,"Prepend or Postpend a NULL character to each character to be sent to the ASCII message"]
[]
["435 / 490 ASCII to PLC Port 5","Value",null,"Help Descriptions"]
["Enabled","Enabled"]
["Data Type","STRING",null,"Data Type of the Tag / File in the PLC"]
["Tag / File Name",null,null,"Controller Scope Tag / File defined in the PLC. If using Program Scope Tag, refer to Appendix D in the userguide"]
["Character Count",82,null,"End Case 1: Max number of characters that can be received to call a message complete. If above 82 and a STRING data type used, refer to Appendix C in the userguide"]
["Timer",0,null,"End Case 2: Max number of time, in milliseconds, that the gateway will wait between receiving ASCII characters. If the time expires, the message is called complete"]
["Start Delimiter Count",0,null,"End Case 3: ASCII message has common start delimiters at the beginning of every message"]
["Start Delimiter 1","[NUL] 0 0x00"]
["Start Delimiter 2","[NUL] 0 0x00"]
["End Delimiter Count",0,null,"End Case 3: ASCII message has common end delimiters at the beginning of every message"]
["End Delimiter 1","[NUL] 0 0x00"]
["End Delimiter 2","[NUL] 0 0x00"]
["Remove Delimiters","Disabled",null,"If using Start or End Delimiters and you don't want them transferred to the PLC, enable this option"]
["Queue Size",5,null,"Enter in the number of complete messages that you want the gateway to hold on to"]
["Queue Full Behavior","Discard New Data",null,"Based on the Queue Size, if the Queue is full, the gateway will discard messaages based on this option"]
["NULL Character Handling","None",null,"Remove all NULL characters prior to sending the message to the PLC"]
[]
["435 / 490 PLC to ASCII Port 5","Value",null,"Help Descriptions"]
["Enabled","Enabled"]
["Data Type","STRING",null,"Data Type of the Tag / File in the PLC"]
["Tag / File Name",null,null,"Controller Scope Tag / File defined in the PLC. If using Program Scope Tag, refer to Appendix D in the userguide"]
["Character Count",82,null,"Max number of characters that can be received from the PLC. If above 82 and a STRING data type used, refer to Appendix C in the userguide"]
["Start Delimiter Count",0,null,"If the ASCII message has common start delimiters at the beginning of every message, then the gateway can be configured for up to 2 start delimiters"]
["Start Delimiter 1","[NUL] 0 0x00"]
["Start Delimiter 2","[NUL] 0 0x00"]
["End Delimiter Count",0,null,"If the ASCII message has common end delimiters at the end of every message, then the gateway can be configured for up to 2 end delimiters"]
["End Delimiter 1","[NUL] 0 0x00"]
["End Delimiter 2","[NUL] 0 0x00"]
["NULL Character Handling","None",null,"Prepend or Postpend a NULL character to each character to be sent to the ASCII message"]
[]
["435 / 490 ASCII to PLC Port 6","Value",null,"Help Descriptions"]
["Enabled","Enabled"]
["Data Type","STRING",null,"Data Type of the Tag / File in the PLC"]
["Tag / File Name",null,null,"Controller Scope Tag / File defined in the PLC. If using Program Scope Tag, refer to Appendix D in the userguide"]
["Character Count",82,null,"End Case 1: Max number of characters that can be received to call a message complete. If above 82 and a STRING data type used, refer to Appendix C in the userguide"]
["Timer",0,null,"End Case 2: Max number of time, in milliseconds, that the gateway will wait between receiving ASCII characters. If the time expires, the message is called complete"]
["Start Delimiter Count",0,null,"End Case 3: ASCII message has common start delimiters at the beginning of every message"]
["Start Delimiter 1","[NUL] 0 0x00"]
["Start Delimiter 2","[NUL] 0 0x00"]
["End Delimiter Count",0,null,"End Case 3: ASCII message has common end delimiters at the beginning of every message"]
["End Delimiter 1","[NUL] 0 0x00"]
["End Delimiter 2","[NUL] 0 0x00"]
["Remove Delimiters","Disabled",null,"If using Start or End Delimiters and you don't want them transferred to the PLC, enable this option"]
["Queue Size",5,null,"Enter in the number of complete messages that you want the gateway to hold on to"]
["Queue Full Behavior","Discard New Data",null,"Based on the Queue Size, if the Queue is full, the gateway will discard messaages based on this option"]
["NULL Character Handling","None",null,"Remove all NULL characters prior to sending the message to the PLC"]
[]
["435 / 490 PLC to ASCII Port 6","Value",null,"Help Descriptions"]
["Enabled","Enabled"]
["Data Type","STRING",null,"Data Type of the Tag / File in the PLC"]
["Tag / File Name",null,null,"Controller Scope Tag / File defined in the PLC. If using Program Scope Tag, refer to Appendix D in the userguide"]
["Character Count",82,null,"Max number of characters that can be received from the PLC. If above 82 and a STRING data type used, refer to Appendix C in the userguide"]
["Start Delimiter Count",0,null,"If the ASCII message has common start delimiters at the beginning of every message, then the gateway can be configured for up to 2 start delimiters"]
["Start Delimiter 1","[NUL] 0 0x00"]
["Start Delimiter 2","[NUL] 0 0x00"]
["End Delimiter Count",0,null,"If the ASCII message has common end delimiters at the end of every message, then the gateway can be configured for up to 2 end delimiters"]
["End Delimiter 1","[NUL] 0 0x00"]
["End Delimiter 2","[NUL] 0 0x00"]
["NULL Character Handling","None",null,"Prepend or Postpend a NULL character to each character to be sent to the ASCII message"]
[]
["435 / 490 ASCII to PLC Port 7","Value",null,"Help Descriptions"]
["Enabled","Enabled"]
["Data Type","STRING",null,"Data Type of the Tag / File in the PLC"]
["Tag / File Name",null,null,"Controller Scope Tag / File defined in the PLC. If using Program Scope Tag, refer to Appendix D in the userguide"]
["Character Count",82,null,"End Case 1: Max number of characters that can be received to call a message complete. If above 82 and a STRING data type used, refer to Appendix C in the userguide"]
["Timer",0,null,"End Case 2: Max number of time, in milliseconds, that the gateway will wait between receiving ASCII characters. If the time expires, the message is called complete"]
["Start Delimiter Count",0,null,"End Case 3: ASCII message has common start delimiters at the beginning of every message"]
["Start Delimiter 1","[NUL] 0 0x00"]
["Start Delimiter 2","[NUL] 0 0x00"]
["End Delimiter Count",0,null,"End Case 3: ASCII message has common end delimiters at the beginning of every message"]
["End Delimiter 1","[NUL] 0 0x00"]
["End Delimiter 2","[NUL] 0 0x00"]
["Remove Delimiters","Disabled",null,"If using Start or End Delimiters and you don't want them transferred to the PLC, enable this option"]
["Queue Size",5,null,"Enter in the number of complete messages that you want the gateway to hold on to"]
["Queue Full Behavior","Discard New Data",null,"Based on the Queue Size, if the Queue is full, the gateway will discard messaages based on this option"]
["NULL Character Handling","None",null,"Remove all NULL characters prior to sending the message to the PLC"]
[]
["435 / 490 PLC to ASCII Port 7","Value",null,"Help Descriptions"]
["Enabled","Enabled"]
["Data Type","STRING",null,"Data Type of the Tag / File in the PLC"]
["Tag / File Name",null,null,"Controller Scope Tag / File defined in the PLC. If using Program Scope Tag, refer to Appendix D in the userguide"]
["Character Count",82,null,"Max number of characters that can be received from the PLC. If above 82 and a STRING data type used, refer to Appendix C in the userguide"]
["Start Delimiter Count",0,null,"If the ASCII message has common start delimiters at the beginning of every message, then the gateway can be configured for up to 2 start delimiters"]
["Start Delimiter 1","[NUL] 0 0x00"]
["Start Delimiter 2","[NUL] 0 0x00"]
["End Delimiter Count",0,null,"If the ASCII message has common end delimiters at the end of every message, then the gateway can be configured for up to 2 end delimiters"]
["End Delimiter 1","[NUL] 0 0x00"]
["End Delimiter 2","[NUL] 0 0x00"]
["NULL Character Handling","None",null,"Prepend or Postpend a NULL character to each character to be sent to the ASCII message"]
[]
["435 / 490 ASCII to PLC Port 8","Value",null,"Help Descriptions"]
["Enabled","Enabled"]
["Data Type","STRING",null,"Data Type of the Tag / File in the PLC"]
["Tag / File Name",null,null,"Controller Scope Tag / File defined in the PLC. If using Program Scope Tag, refer to Appendix D in the userguide"]
["Character Count",82,null,"End Case 1: Max number of characters that can be received to call a message complete. If above 82 and a STRING data type used, refer to Appendix C in the userguide"]
["Timer",0,null,"End Case 2: Max number of time, in milliseconds, that the gateway will wait between receiving ASCII characters. If the time expires, the message is called complete"]
["Start Delimiter Count",0,null,"End Case 3: ASCII message has common start delimiters at the beginning of every message"]
["Start Delimiter 1","[NUL] 0 0x00"]
["Start Delimiter 2","[NUL] 0 0x00"]
["End Delimiter Count",0,null,"End Case 3: ASCII message has common end delimiters at the beginning of every message"]
["End Delimiter 1","[NUL] 0 0x00"]
["End Delimiter 2","[NUL] 0 0x00"]
["Remove Delimiters","Disabled",null,"If using Start or End Delimiters and you don't want them transferred to the PLC, enable this option"]
["Queue Size",5,null,"Enter in the number of complete messages that you want the gateway to hold on to"]
["Queue Full Behavior","Discard New Data",null,"Based on the Queue Size, if the Queue is full, the gateway will discard messaages based on this option"]
["NULL Character Handling","None",null,"Remove all NULL characters prior to sending the message to the PLC"]
[]
["435 / 490 PLC to ASCII Port 8","Value",null,"Help Descriptions"]
["Enabled","Enabled"]
["Data Type","STRING",null,"Data Type of the Tag / File in the PLC"]
["Tag / File Name",null,null,"Controller Scope Tag / File defined in the PLC. If using Program Scope Tag, refer to Appendix D in the userguide"]
["Character Count",82,null,"Max number of characters that can be received from the PLC. If above 82 and a STRING data type used, refer to Appendix C in the userguide"]
["Start Delimiter Count",0,null,"If the ASCII message has common start delimiters at the beginning of every message, then the gateway can be configured for up to 2 start delimiters"]
["Start Delimiter 1","[NUL] 0 0x00"]
["Start Delimiter 2","[NUL] 0 0x00"]
["End Delimiter Count",0,null,"If the ASCII message has common end delimiters at the end of every message, then the gateway can be configured for up to 2 end delimiters"]
["End Delimiter 1","[NUL] 0 0x00"]
["End Delimiter 2","[NUL] 0 0x00"]
["NULL Character Handling","None",null,"Prepend or Postpend a NULL character to each character to be sent to the ASCII message"]
[]
["435 / 490 ASCII to PLC Port 9","Value",null,"Help Descriptions"]
["Enabled","Enabled"]
["Data Type","STRING",null,"Data Type of the Tag / File in the PLC"]
["Tag / File Name",null,null,"Controller Scope Tag / File defined in the PLC. If using Program Scope Tag, refer to Appendix D in the userguide"]
["Character Count",82,null,"End Case 1: Max number of characters that can be received to call a message complete. If above 82 and a STRING data type used, refer to Appendix C in the userguide"]
["Timer",0,null,"End Case 2: Max number of time, in milliseconds, that the gateway will wait between receiving ASCII characters. If the time expires, the message is called complete"]
["Start Delimiter Count",0,null,"End Case 3: ASCII message has common start delimiters at the beginning of every message"]
["Start Delimiter 1","[NUL] 0 0x00"]
["Start Delimiter 2","[NUL] 0 0x00"]
["End Delimiter Count",0,null,"End Case 3: ASCII message has common end delimiters at the beginning of every message"]
["End Delimiter 1","[NUL] 0 0x00"]
["End Delimiter 2","[NUL] 0 0x00"]
["Remove Delimiters","Disabled",null,"If using Start or End Delimiters and you don't want them transferred to the PLC, enable this option"]
["Queue Size",5,null,"Enter in the number of complete messages that you want the gateway to hold on to"]
["Queue Full Behavior","Discard New Data",null,"Based on the Queue Size, if the Queue is full, the gateway will discard messaages based on this option"]
["NULL Character Handling","None",null,"Remove all NULL characters prior to sending the message to the PLC"]
[]
["435 / 490 PLC to ASCII Port 9","Value",null,"Help Descriptions"]
["Enabled","Enabled"]
["Data Type","STRING",null,"Data Type of the Tag / File in the PLC"]
["Tag / File Name",null,null,"Controller Scope Tag / File defined in the PLC. If using Program Scope Tag, refer to Appendix D in the userguide"]
["Character Count",82,null,"Max number of characters that can be received from the PLC. If above 82 and a STRING data type used, refer to Appendix C in the userguide"]
["Start Delimiter Count",0,null,"If the ASCII message has common start delimiters at the beginning of every message, then the gateway can be configured for up to 2 start delimiters"]
["Start Delimiter 1","[NUL] 0 0x00"]
["Start Delimiter 2","[NUL] 0 0x00"]
["End Delimiter Count",0,null,"If the ASCII message has common end delimiters at the end of every message, then the gateway can be configured for up to 2 end delimiters"]
["End Delimiter 1","[NUL] 0 0x00"]
["End Delimiter 2","[NUL] 0 0x00"]
["NULL Character Handling","None",null,"Prepend or Postpend a NULL character to each character to be sent to the ASCII message"]

{"sheet":"Overall","index":1,"n_rows":5,"n_cols":1,"rows_kept":5,"cut":false,"hidden":true,"merged":[]}
["Read / Write"]
["None"]
["Read"]
["Write"]
["Read/Write"]

{"sheet":"435_490_Configuration","index":2,"n_rows":266,"n_cols":13,"rows_kept":266,"cut":false,"hidden":true,"merged":[]}
["Auto-Negotiate",null,"PLC Type",null,"PLC Mode"]
["10 Half",null,"None",null,"UCMM"]
["10 Full",null,"CompactLogix",null,"Class 3"]
["100 Half",null,"ControlLogix"]
["100 Full",null,"FlexLogix"]
["Auto Negotiate",null,"MicroLogix"]
[null,null,"PLC5E"]
[null,null,"SLC"]
[]
["ASCII",null,"ASCII Data Type",null,"ASCII Delimiter Count",null,"ASCII Delimiter",null,"ASCII Queue Behavior",null,"ASCII A2C NULL",null,"ASCII C2A NULL"]
["Enabled",null,"STRING",null,0,null,"[NUL] 0 0x00",null,"Discard New Data",null,"None",null,"None"]
["Disabled",null,"INT",null,1,null,"[SOH] 1 0x01",null,"Overwrite Oldest Data",null,"Remove NULL",null,"Prepend NULL"]
[null,null,"SINT",null,2,null,"[STX] 2 0x02",null,null,null,null,null,"Postpend NULL"]
[null,null,null,null,null,null,"[ETX] 3 0x03"]
[null,null,null,null,null,null,"[EOT] 4 0x04"]
[null,null,null,null,null,null,"[ENQ] 5 0x05"]
[null,null,null,null,null,null,"[ACK] 6 0x06"]
[null,null,null,null,null,null,"[BEL] 7 0x07"]
[null,null,null,null,null,null,"[BS] 8 0x08"]
[null,null,null,null,null,null,"[HT] 9 0x09"]
[null,null,null,null,null,null,"[LF] 10 0x0A"]
[null,null,null,null,null,null,"[VT] 11 0x0B"]
[null,null,null,null,null,null,"[FF] 12 0x0C"]
[null,null,null,null,null,null,"[CR] 13 0x0D"]
[null,null,null,null,null,null,"[SO] 14 0x0E"]
[null,null,null,null,null,null,"[SI] 15 0x0F"]
[null,null,null,null,null,null,"[DLE] 16 0x10"]
[null,null,null,null,null,null,"[DC1] 17 0x11"]
[null,null,null,null,null,null,"[DC2] 18 0x12"]
[null,null,null,null,null,null,"[DC3] 19 0x13"]
[null,null,null,null,null,null,"[DC4] 20 0x14"]
[null,null,null,null,null,null,"[NAK] 21 0x15"]
[null,null,null,null,null,null,"[SYN] 22 0x16"]
[null,null,null,null,null,null,"[ETB] 23 0x17"]
[null,null,null,null,null,null,"[CAN] 24 0x18"]
[null,null,null,null,null,null,"[EM] 25 0x19"]
[null,null,null,null,null,null,"[SUB] 26 0x1A"]
[null,null,null,null,null,null,"[ESC] 27 0x1B"]
[null,null,null,null,null,null,"[FS] 28 0x1C"]
[null,null,null,null,null,null,"[GS] 29 0x1D"]
[null,null,null,null,null,null,"[RS] 30 0x1E"]
[null,null,null,null,null,null,"[US] 31 0x1F"]
[null,null,null,null,null,null,"[SP] 32 0x20"]
[null,null,null,null,null,null,"! 33 0x21"]
[null,null,null,null,null,null,"\" 34 0x22"]
[null,null,null,null,null,null,"# 35 0x23"]
[null,null,null,null,null,null,"$ 36 0x24"]
[null,null,null,null,null,null,"% 37 0x25"]
[null,null,null,null,null,null,"& 38 0x26"]
[null,null,null,null,null,null,"' 39 0x27"]
[null,null,null,null,null,null,"( 40 0x28"]
[null,null,null,null,null,null,") 41 0x29"]
[null,null,null,null,null,null,"* 42 0x2A"]
[null,null,null,null,null,null,"+ 43 0x2B"]
[null,null,null,null,null,null,", 44 0x2C"]
[null,null,null,null,null,null,"- 45 0x2D"]
[null,null,null,null,null,null,". 46 0x2E"]
[null,null,null,null,null,null,"/ 47 0x2F"]
[null,null,null,null,null,null,"0 48 0x30"]
[null,null,null,null,null,null,"1 49 0x31"]
[null,null,null,null,null,null,"2 50 0x32"]
[null,null,null,null,null,null,"3 51 0x33"]
[null,null,null,null,null,null,"4 52 0x34"]
[null,null,null,null,null,null,"5 53 0x35"]
[null,null,null,null,null,null,"6 54 0x36"]
[null,null,null,null,null,null,"7 55 0x37"]
[null,null,null,null,null,null,"8 56 0x38"]
[null,null,null,null,null,null,"9 57 0x39"]
[null,null,null,null,null,null,": 58 0x3A"]
[null,null,null,null,null,null,"; 59 0x3B"]
[null,null,null,null,null,null,"< 60 0x3C"]
[null,null,null,null,null,null,"= 61 0x3D"]
[null,null,null,null,null,null,"> 62 0x3E"]
[null,null,null,null,null,null,"? 63 0x3F"]
[null,null,null,null,null,null,"@ 64 0x40"]
[null,null,null,null,null,null,"A 65 0x41"]
[null,null,null,null,null,null,"B 66 0x42"]
[null,null,null,null,null,null,"C 67 0x43"]
[null,null,null,null,null,null,"D 68 0x44"]
["E",null,null,null,null,null,"E 69 0x45"]
[null,null,null,null,null,null,"F 70 0x46"]
[null,null,null,null,null,null,"G 71 0x47"]
[null,null,null,null,null,null,"H 72 0x48"]
[null,null,null,null,null,null,"I 73 0x49"]
[null,null,null,null,null,null,"J 74 0x4A"]
[null,null,null,null,null,null,"K 75 0x4B"]
[null,null,null,null,null,null,"L 76 0x4C"]
[null,null,null,null,null,null,"M 77 0x4D"]
[null,null,null,null,null,null,"N 78 0x4E"]
[null,null,null,null,null,null,"O 79 0x4F"]
[null,null,null,null,null,null,"P 80 0x50"]
[null,null,null,null,null,null,"Q 81 0x51"]
[null,null,null,null,null,null,"R 82 0x52"]
[null,null,null,null,null,null,"S 83 0x53"]
[null,null,null,null,null,null,"T 84 0x54"]
[null,null,null,null,null,null,"U 85 0x55"]
[null,null,null,null,null,null,"V 86 0x56"]
[null,null,null,null,null,null,"W 87 0x57"]
[null,null,null,null,null,null,"X 88 0x58"]
[null,null,null,null,null,null,"Y 89 0x59"]
[null,null,null,null,null,null,"Z 90 0x5A"]
[null,null,null,null,null,null,"[ 91 0x5B"]
[null,null,null,null,null,null,"\\ 92 0x5C"]
[null,null,null,null,null,null,"] 93 0x5D"]
[null,null,null,null,null,null,"^ 94 0x5E"]
[null,null,null,null,null,null,"_ 95 0x5F"]
[null,null,null,null,null,null,"` 96 0x60"]
[null,null,null,null,null,null,"a 97 0x61"]
[null,null,null,null,null,null,"b 98 0x62"]
[null,null,null,null,null,null,"c 99 0x63"]
[null,null,null,null,null,null,"d 100 0x64"]
[null,null,null,null,null,null,"e 101 0x65"]
[null,null,null,null,null,null,"f 102 0x66"]
[null,null,null,null,null,null,"g 103 0x67"]
[null,null,null,null,null,null,"h 104 0x68"]
[null,null,null,null,null,null,"i 105 0x69"]
[null,null,null,null,null,null,"j 106 0x6A"]
[null,null,null,null,null,null,"k 107 0x6B"]
[null,null,null,null,null,null,"l 108 0x6C"]
[null,null,null,null,null,null,"m 109 0x6D"]
[null,null,null,null,null,null,"n 110 0x6E"]
[null,null,null,null,null,null,"o 111 0x6F"]
[null,null,null,null,null,null,"p 112 0x70"]
[null,null,null,null,null,null,"q 113 0x71"]
[null,null,null,null,null,null,"r 114 0x72"]
[null,null,null,null,null,null,"s 115 0x73"]
[null,null,null,null,null,null,"t 116 0x74"]
[null,null,null,null,null,null,"u 117 0x75"]
[null,null,null,null,null,null,"v 118 0x76"]
[null,null,null,null,null,null,"w 119 0x77"]
[null,null,null,null,null,null,"x 120 0x78"]
[null,null,null,null,null,null,"y 121 0x79"]
[null,null,null,null,null,null,"z 122 0x7A"]
[null,null,null,null,null,null,"{ 123 0x7B"]
[null,null,null,null,null,null,"| 124 0x7C"]
[null,null,null,null,null,null,"} 125 0x7D"]
[null,null,null,null,null,null,"~ 126 0x7E"]
[null,null,null,null,null,null,". 127 0x7F"]
[null,null,null,null,null,null,". 128 0x80"]
[null,null,null,null,null,null,". 129 0x81"]
[null,null,null,null,null,null,". 130 0x82"]
[null,null,null,null,null,null,". 131 0x83"]
[null,null,null,null,null,null,". 132 0x84"]
[null,null,null,null,null,null,". 133 0x85"]
[null,null,null,null,null,null,". 134 0x86"]
[null,null,null,null,null,null,". 135 0x87"]
[null,null,null,null,null,null,". 136 0x88"]
[null,null,null,null,null,null,". 137 0x89"]
[null,null,null,null,null,null,". 138 0x8A"]
[null,null,null,null,null,null,". 139 0x8B"]
[null,null,null,null,null,null,". 140 0x8C"]
[null,null,null,null,null,null,". 141 0x8D"]
[null,null,null,null,null,null,". 142 0x8E"]
[null,null,null,null,null,null,". 143 0x8F"]
[null,null,null,null,null,null,". 144 0x90"]
[null,null,null,null,null,null,". 145 0x91"]
[null,null,null,null,null,null,". 146 0x92"]
[null,null,null,null,null,null,". 147 0x93"]
[null,null,null,null,null,null,". 148 0x94"]
[null,null,null,null,null,null,". 149 0x95"]
[null,null,null,null,null,null,". 150 0x96"]
[null,null,null,null,null,null,". 151 0x97"]
[null,null,null,null,null,null,". 152 0x98"]
[null,null,null,null,null,null,". 153 0x99"]
[null,null,null,null,null,null,". 154 0x9A"]
[null,null,null,null,null,null,". 155 0x9B"]
[null,null,null,null,null,null,". 156 0x9C"]
[null,null,null,null,null,null,". 157 0x9D"]
[null,null,null,null,null,null,". 158 0x9E"]
[null,null,null,null,null,null,". 159 0x9F"]
[null,null,null,null,null,null,". 160 0xA0"]
[null,null,null,null,null,null,". 161 0xA1"]
[null,null,null,null,null,null,". 162 0xA2"]
[null,null,null,null,null,null,". 163 0xA3"]
[null,null,null,null,null,null,". 164 0xA4"]
[null,null,null,null,null,null,". 165 0xA5"]
[null,null,null,null,null,null,". 166 0xA6"]
[null,null,null,null,null,null,". 167 0xA7"]
[null,null,null,null,null,null,". 168 0xA8"]
[null,null,null,null,null,null,". 169 0xA9"]
[null,null,null,null,null,null,". 170 0xAA"]
[null,null,null,null,null,null,". 171 0xAB"]
[null,null,null,null,null,null,". 172 0xAC"]
[null,null,null,null,null,null,". 173 0xAD"]
[null,null,null,null,null,null,". 174 0xAE"]
[null,null,null,null,null,null,". 175 0xAF"]
[null,null,null,null,null,null,". 176 0xB0"]
[null,null,null,null,null,null,". 177 0xB1"]
[null,null,null,null,null,null,". 178 0xB2"]
[null,null,null,null,null,null,". 179 0xB3"]
[null,null,null,null,null,null,". 180 0xB4"]
[null,null,null,null,null,null,". 181 0xB5"]
[null,null,null,null,null,null,". 182 0xB6"]
[null,null,null,null,null,null,". 183 0xB7"]
[null,null,null,null,null,null,". 184 0xB8"]
[null,null,null,null,null,null,". 185 0xB9"]
[null,null,null,null,null,null,". 186 0xBA"]
[null,null,null,null,null,null,". 187 0xBB"]
[null,null,null,null,null,null,". 188 0xBC"]
[null,null,null,null,null,null,". 189 0xBD"]
[null,null,null,null,null,null,". 190 0xBE"]
[null,null,null,null,null,null,". 191 0xBF"]
[null,null,null,null,null,null,". 192 0xC0"]
[null,null,null,null,null,null,". 193 0xC1"]
[null,null,null,null,null,null,". 194 0xC2"]
[null,null,null,null,null,null,". 195 0xC3"]
[null,null,null,null,null,null,". 196 0xC4"]
[null,null,null,null,null,null,". 197 0xC5"]
[null,null,null,null,null,null,". 198 0xC6"]
[null,null,null,null,null,null,". 199 0xC7"]
[null,null,null,null,null,null,". 200 0xC8"]
[null,null,null,null,null,null,". 201 0xC9"]
[null,null,null,null,null,null,". 202 0xCA"]
[null,null,null,null,null,null,". 203 0xCB"]
[null,null,null,null,null,null,". 204 0xCC"]
[null,null,null,null,null,null,". 205 0xCD"]
[null,null,null,null,null,null,". 206 0xCE"]
[null,null,null,null,null,null,". 207 0xCF"]
[null,null,null,null,null,null,". 208 0xD0"]
[null,null,null,null,null,null,". 209 0xD1"]
[null,null,null,null,null,null,". 210 0xD2"]
[null,null,null,null,null,null,". 211 0xD3"]
[null,null,null,null,null,null,". 212 0xD4"]
[null,null,null,null,null,null,". 213 0xD5"]
[null,null,null,null,null,null,". 214 0xD6"]
[null,null,null,null,null,null,". 215 0xD7"]
[null,null,null,null,null,null,". 216 0xD8"]
[null,null,null,null,null,null,". 217 0xD9"]
[null,null,null,null,null,null,". 218 0xDA"]
[null,null,null,null,null,null,". 219 0xDB"]
[null,null,null,null,null,null,". 220 0xDC"]
[null,null,null,null,null,null,". 221 0xDD"]
[null,null,null,null,null,null,". 222 0xDE"]
[null,null,null,null,null,null,". 223 0xDF"]
[null,null,null,null,null,null,". 224 0xE0"]
[null,null,null,null,null,null,". 225 0xE1"]
[null,null,null,null,null,null,". 226 0xE2"]
[null,null,null,null,null,null,". 227 0xE3"]
[null,null,null,null,null,null,". 228 0xE4"]
[null,null,null,null,null,null,". 229 0xE5"]
[null,null,null,null,null,null,". 230 0xE6"]
[null,null,null,null,null,null,". 231 0xE7"]
[null,null,null,null,null,null,". 232 0xE8"]
[null,null,null,null,null,null,". 233 0xE9"]
[null,null,null,null,null,null,". 234 0xEA"]
[null,null,null,null,null,null,". 235 0xEB"]
[null,null,null,null,null,null,". 236 0xEC"]
[null,null,null,null,null,null,". 237 0xED"]
[null,null,null,null,null,null,". 238 0xEE"]
[null,null,null,null,null,null,". 239 0xEF"]
[null,null,null,null,null,null,". 240 0xF0"]
[null,null,null,null,null,null,". 241 0xF1"]
[null,null,null,null,null,null,". 242 0xF2"]
[null,null,null,null,null,null,". 243 0xF3"]
[null,null,null,null,null,null,". 244 0xF4"]
[null,null,null,null,null,null,". 245 0xF5"]
[null,null,null,null,null,null,". 246 0xF6"]
[null,null,null,null,null,null,". 247 0xF7"]
[null,null,null,null,null,null,". 248 0xF8"]
[null,null,null,null,null,null,". 249 0xF9"]
[null,null,null,null,null,null,". 250 0xFA"]
[null,null,null,null,null,null,". 251 0xFB"]
[null,null,null,null,null,null,". 252 0xFC"]
[null,null,null,null,null,null,". 253 0xFD"]
[null,null,null,null,null,null,". 254 0xFE"]
[null,null,null,null,null,null,". 255 0xFF"]

{"sheet":"Serial_Configuration","index":3,"n_rows":101,"n_cols":3,"rows_kept":101,"cut":false,"hidden":true,"merged":[]}
["Hardware Selection"]
["N72"]
["N700"]
["N34"]
["NNA1"]
["NNA4"]
["NNAU"]
["N70U"]
["N70L"]
["N70PB"]
["N2E"]
[]
["Comms Mode N72 - Port 0",null,"Comms Mode N72 - Port 1"]
["RS232",null,"RS232"]
["RS485"]
["RS422"]
[]
["Comms Mode N700 - Port 0",null,"Comms Mode N700 - Port 1"]
["RS232",null,"RS232"]
["RS485"]
["RS422"]
[]
["Comms Mode N34 - Port 0",null,"Comms Mode N34 - Port 1"]
["RS232",null,"RS232"]
["RS485",null,"RS485"]
["RS422",null,"RS422"]
[]
["Comms Mode NNA1 - Port 0",null,"Comms Mode NNA1 - Port 1"]
["RS232"]
["RS485"]
[]
["Comms Mode NNA4 - Port 0",null,"Comms Mode NNA4 - Port 1"]
["RS485",null,"RS485"]
[]
["Comms Mode NNAU - Port 0",null,"Comms Mode NNAU - Port 1"]
[]
[]
["Comms Mode N70U - Port 0",null,"Comms Mode N70U - Port 1"]
["RS485"]
[]
["Comms Mode N70L - Port 0",null,"Comms Mode N70L - Port 1"]
["RS232"]
["RS485"]
["RS422"]
[]
["Comms Mode N70PB - Port 0",null,"Comms Mode N70PB - Port 1"]
["RS232"]
["RS485"]
["RS422"]
[]
["Comms Mode N2E - Port 0",null,"Comms Mode N2E - Port 1"]
["RS232"]
["RS485"]
["RS422"]
[]
["Serial"]
["Enabled"]
["Disabled"]
[]
["Serial Mode"]
["RS232"]
["RS485"]
["RS422"]
[]
["Serial Baud"]
[110]
[300]
[600]
[1200]
[2400]
[4800]
[9600]
[14400]
[19200]
[28800]
[38400]
[56000]
[57600]
[62500]
[76800]
[115200]
[]
["Serial Data Bits"]
[5]
[6]
[7]
[8]
[]
["Serial Stop Bits"]
[1]
[2]
[]
["Serial Parity"]
["NONE"]
["EVEN"]
["ODD"]
[]
["Serial Flow Control"]
["NONE"]
["Xon/Xoff"]
["Rts/Cts"]

{"sheet":"TCPIP_Configuration","index":4,"n_rows":7,"n_cols":1,"rows_kept":7,"cut":false,"hidden":true,"merged":[]}
["TCP/IP"]
["Enabled"]
["Disabled"]
[]
["TCP/IP Client"]
["Enabled"]
["Disabled"]

{"sheet":"Product_Selector","index":5,"n_rows":12,"n_cols":1,"rows_kept":12,"cut":false,"hidden":true,"merged":[]}
["Product"]
["435NBX-N700"]
["435NBX-NNA1"]
["435NBX-N72"]
["435NBX-NNA4"]
["435NBX-N34"]
["435USB-NNAU"]
["490NBX-N700"]
["490NBX-NNA1"]
["490NBX-N72"]
["490NBX-NNA4"]
["490NBX-N34"]